## Sheet1
|  | Capital Charge Rate = | 13.2% | For retrofit FGD costs, see:
|  | Annual Capacity Factor = | 70% | EPA Power Sector Modeling Platform v.5.13, Documentation, Chapter 5, Table 5-3
|  | Coal Heat Rate, Btu/kWh HHV = | 10000 | http://www.epa.gov/airmarkets/documents/ipm/Chapter_5.pdf
Coal - FGD retrofits |  |  | Wet FGD |  |  | Dry FGD
|  | MW | 300 | 500 | 700 | 300 | 500 | 700
FGD Retrofit Costs |  | 2011$
| Capital Cost | $/kW | 629 | 544 | 495 | 538 | 465 | 442
|  | $/kW-yr | 83.028 | 71.808 | 65.34 | 71.016 | 61.38 | 58.344
| Fixed O&M Cost | $/kW-yr | 12 | 9 | 8 | 9 | 7 | 6
| Variable O&M Cost | $/MWh | 2.3 | 2.3 | 2.3 | 2.8 | 2.8 | 2.8
|  | $/kW-yr | 14.1036 | 14.1036 | 14.1036 | 17.1696 | 17.1696 | 17.1696
| Total Cost | $/kW-yr | 109.1316 | 94.9116 | 87.4436 | 97.1856 | 85.5496 | 81.5136
SO2 Control Costs
| Uncontrolled SO2 | lb/MMBtu | 2.5 | 2.5 | 2.5 | 1.5 | 1.5 | 1.5
| Removal rate | % | 96% | 96% | 96% | 92% | 92% | 92%
| SO2 removed | lb/MMBtu | 2.4 | 2.4 | 2.4 | 1.38 | 1.38 | 1.38
| SO2 or NOx emission | lb/MMBtu | 0.1 | 0.1 | 0.1 | 0.12 | 0.12 | 0.12
| SO2 removed | lb/MWh | 24 | 24 | 24 | 13.8 | 13.8 | 13.8
| SO2 removed | ton/kW-yr | 0.073584 | 0.073584 | 0.073584 | 0.042311 | 0.042311 | 0.042311
| SO2 Total Cost | $/ton | 1483.0887 | 1289.8402 | 1188.3507 | 2296.9455 | 2021.9329 | 1926.5436
| SO2 Total Cost | $/kW-yr | 109.1316 | 94.9116 | 87.4436 | 97.1856 | 85.5496 | 81.5136
| SO2 Total Cost | $/MWh | 17.7971 | 15.4781 | 14.2602 | 15.8489 | 13.9513 | 13.2932
CO2 Control Costs |  |  | Coal-steam |  |  |  | NGCC | 7800 | = NGCC Heat Rate**, Btu/kWh HHV
| Uncontrolled CO2* | lb/MMBtu | 203.8518 | 203.8518 | 203.8518 | 203.8518 | 116.5373 | ** adjusted to give about 900 for uncontrolled CO2 lb/MWh
| Uncontrolled CO2 | lb/MWh | 2038.5176 | 2038.5176 | 2038.5176 | 2038.5176 | 908.9909 | <-- fleet avg in 2012 was 902
| Uncontrolled CO2 | ton/kW-yr | 6.2501 | 6.2501 | 6.2501 | 6.2501 | 2.787
| Controlled CO2 | lb/MWh | 1305 | 1305 | 1305 | 1305 | 771
| CO2 avoided | % | 35.98% | 35.98% | 35.98% | 35.98% | 15.18%
| Avoided CO2 | ton/kW-yr | 2.249 | 2.249 | 2.249 | 2.249 | 0.42308
| CO2 control cost | $/ton | 23 | 24 | 37 | 30 | 37
| CO2 control cost | $/kW-yr | 51.7262 | 53.9752 | 83.2117 | 67.4689 | 15.654
| CO2 control cost | $/MWh | 8.4355 | 8.8022 | 13.5701 | 11.0028 | 2.5528
* For Coal-steam CO2 calc, assumed coal is EPRI ILL#6, C = 61%wt, HHV=10,982Btu/lb
* For NGCC CO2 calc, assumed gas is B&W41, C = 69.3%wt, HHV=21,824Btu/lb